CHANGE THIS TITLE TO COMPANY NAME & ADDRESS

This Logbook should be kept up to date and made Available for inspection by the Fire Authority

| Property / Business Name |  |
| --- | --- |
| Address Line 1 |  |
| Address Line 2 |  |
| Town |  |
| Post Code |  |
| Contact Name 1 |  |
| Contact Name 2 |  |

Contents

1.	Useful Telephone Contacts	3

2.	Fire Safety Legislation	4

Regulatory Reform (Fire Safety) Order 2005	4

Building Safety Act 2022	5

Fire Safety (England) Regulations 2022	5

3.	General Fire Safety Requirements	7

4.	Fire Alarm System	9

Record of Fire Alarm Test	10

5.	Unwanted Fire Signals	11

Record of False Fire Alarm Calls	12

6.	Emergency Lighting System	13

Record of Emergency Lighting System Test	14

7.	Fire Fighting Equipment	15

Record of Fire Fighting Equipment Test	16

8.	Fire Doors – Register and Maintenance	17

Record of Door Check Test	19

Action Plan	20

9.	Acoustic Fire Door Holders Testing	21

Record of Acoustic Fire Door Holders Test	22

10.	Sprinkler Systems	23

Record of Sprinkler System Test	24

11.	Smoke Ventilation Systems	25

Record of Smoke Ventilation System Test	25

12.	Fire Fighting Provisions	26

Record of Fire Fighting Provisions Test	29

Action Plan	31

13.	Fire Instruction and Training	32

Record of Staff Training / Instruction	33

14.	Fire Evacuations and Drills	34

Record of Fire Drills / Evacuations	35

15.	Fire Safety Risk Assessment	36

Record of Fire Safety Risk Assessment	36

16.	Business Continuity and Planning	37

# Useful Telephone Contacts

| Contact | Company | Number |
| --- | --- | --- |
| Fire Alarm Service Engineer |  |  |
| Fire Extinguisher Engineer |  |  |
| Emergency Lighting Engineer |  |  |

For Further Fire Protection Advice Please Contact: ADVICE LINE: 0115 838 8205

E-Mail: fireprotection@notts-fire.gov.uk

Information about Fire Protection or other related matters can be found on the Nottinghamshire Fire & Rescue Service website:

www.notts-fire.gov.uk and at:www.fire.gov.uk

Information and guidance is available in the fire safety guides published by Communities and Local Government:

www.communities.gov.uk

# Fire Safety Legislation

## Regulatory Reform (Fire Safety) Order 2005

The vast majority of sites and premises throughout England & Wales must now conform with the requirements of the Regulatory Reform (Fire Safety) Order, which has replaced the Fire Precautions Act 1971 and the Fire Precautions (Workplace) Regulations 1997, as well as over 100 pieces of legislation relating to Fire Safety.

The Fire Safety Order does not apply to people’s private homes, including individual flats in a block or house, though it does apply to; common areas; shared means of escape and facilities provided to assist the Fire Service, such as dry risers.

This fire safety logbook has been prepared to assist building owners, managers and other responsible persons to co-ordinate and maintain a fire safety record keeping system.

The logbook also seeks to cover the main requirements for demonstrating compliance with current fire safety legislation. It is recommended that it be kept in a loose-leaf format with new record keeping pages photocopied or downloaded when required. The logbook should be kept up to date and readily accessible for inspection by the enforcing authority when required.

In terms of maintaining records, it is important to take note of the following legal requirements;

Article 32 (2) (b) Regulatory Reform (Fire Safety) Order 2005

‘It is an offence to make in any register, book, notice or other document required to be kept, served or given by or under, this Order, an entry which he knows to be false in a material particular.’

Article 17.1 Regulatory Reform (Fire Safety) Order 2005

‘Where necessary in order to safeguard the safety of relevant persons the responsible person must ensure that the premises and any facilities, equipment and devices provided…., are subject to a suitable system of maintenance and are maintained in an efficient state, in efficient working order and in good repair’

The Responsible Person

The Responsible person is defined as any or all of the following;

- The employer, if the workplace is to any extent under his control

- The person who has control of the premises

- The owner

Article 8.1 Regulatory Reform (Fire Safety) Order 2005

The responsible person must:

Take such general fire precautions as will ensure, so far as is reasonably practicable, the safety of any of his employees and in relation to relevant persons who are not his employees, take such general fire precautions as may reasonably be required in the circumstances of the case to ensure the premises are safe.

Competent Person

A competent person is defined as;

A person who is regarded as competent for the purposes of the Fire Safety Order, where they have sufficient training and experience or knowledge and other qualities to enable themselves properly to assist in the undertaking of preventative and protective measures.

Relevant Persons

A relevant person is defined as;

- Any person who is or may be lawfully on the premises

- Any person in the immediate vicinity of the premises who is at risk from a fire on the premises.

## Building Safety Act 2022

From 1 October 2023, new fire safety legislation comes into effect which will impose new duties on businesses and building owners. The Fire Safety Order is the primary fire safety legislation in England and Wales, and it applies to all non-domestic premises as well as the communal parts of residential buildings. Changes to this legislation have been introduced through the Building Safety Act 2022 and represent the next phase of the government's fire safety reform programme.

The main changes introduced by the legislation are:

- Written fire risk assessment and fire safety arrangements:

  - If you are a responsible person, then you will need to record both your fire risk assessment and fire safety arrangement in full, regardless of the size or purpose of the business or premises.

- Enhanced requirements for cooperation and coordination:

  - In premises where there is more than one responsible person (e.g. in multi-occupied premises or buildings where the occupier and building owner are different entities) there are increased requirements for cooperation and coordination between responsible persons.

- Provision of information to residents:

  - In residential buildings with two or more domestic premises (e.g. blocks of flats), the responsible owner must provide residents with information on the risks from fire within their building and the fire safety measures provided to keep them safe.

## Fire Safety (England) Regulations 2022

The Fire Safety (England) Regulations 2022, which came into force in January 2023, mandate that Responsible Persons for multi-occupied residential buildings must implement specific, risk-based fire safety measures. These include routine checks on fire doors, sharing building plans with fire services, and installing signage, not limited to 11m + (or 5 storeys) and high-rise buildings (over 18m or 7 storeys).

Regulation 7 of the Fire Safety (England) Regulations directly relates to Lifts and essential Fire-Fighting Equipment specially upkeeping the maintenance of such equipment and ensuring routine checks are undertaken.

Register of Persons Responsible / Competent for      Management of Fire Precautions

| Date | Name | Responsibility |
| --- | --- | --- |

Legal Fire Safety Requirements

You must:

- Carry out a fire-risk assessment identifying any possible dangers and risks consider who may be especially at risk.

- Remove or reduce the risk from fire as far as is reasonably possible and provide general fire precautions to deal with any possible risk left.

- Take other measures to make sure there is protection if flammable or explosive materials are used or stored.

- Create a plan to deal with any emergency and, in most cases, keep a record of your findings.

- Review your findings when necessary.

# General Fire Safety Requirements

Means of Escape

- Fire doors are provided to prevent the spread of heat and smoke. Keep them shut and

do not prop them open or remove self-closing devices.

- Keep corridors and stairways clear of storage and waste material.

- Ensure that final exit doors can be readily opened from the inside without the use of a key.

- Keep areas outside final exit doors clear of obstructions at all times.

- Always ensure that exits are clearly indicated, with the exit signs visible from the furthermost part of a room.

Fire Alarm System

Always ensure that the fire alarm system is in working order and that staff know how to use it, including what action to take on hearing the alarm.

Fire-Fighting Equipment

- Ensure that all staff know where the extinguishers are sited and how to operate them safely.

- Always ensure that they are inspected and maintained regularly.

Emergency and General Lighting

- Ensure that all lighting systems are checked and maintained regularly.

- Replace any defective bulbs/components immediately.

Instructions to Staff and Guests

Staff will need to be aware of their responsibilities in the event of an emergency. They should know how to:

- Raise the alarm.

- Call the Fire Brigade.

- Know when not to tackle a fire.

- Know the correct evacuation procedures for the premises.

Guests and Visitors

- Ensure that all guests/visitors to the premises are aware of the actions to take in the event of an emergency.

- Premises which take in foreign workers/guests should have their fire instruction notices in a form which is understandable to them (Pictorial for example) or printed in the appropriate language.

Electrical Equipment and Installations

Fires occurring in electrical equipment are increasing due to the improper use, application or lack of maintenance of the equipment. To reduce the risk of fire all electrical appliances should be maintained under the provisions of the Electricity at Work Regulations 1989.

- Wiring should be regularly checked and renewed if necessary.

- Ensure that correct fuses are fitted to all electrical appliances and fuse boxes.

- Disconnect plugs of all appliances from the mains electricity when not in use.

Heating

- Keep boiler houses clear - do not use them as an extra storeroom.

- Keep portable heating appliances away from furniture and any combustible materials.

Smoking Materials

- Smoking is no longer allowed on any premises (see https://www.gov.uk/smoking-at-work- the-law)

- Ensure that the law is enforced in your policies to staff and guests.

- If outside smoking is permitted be vigilant in these designated areas and provide adequate ashtrays as well as ventilation.

Arson

Many arson attacks are preceded by petty vandalism and theft, moving onto small fires, which get bigger and more ambitious over a period of time. The proper management of waste materials can remove an easy opportunity target of the arsonist, deliberate fires set in combustible materials next to buildings can quickly spread to the premises themselves which can lead to a complete loss of the building and even the business itself. Help to protect your premises against arson by;

- Locking away any flammable liquids or gases

- Effectively secure your premises at the end of the day

- Keep refuse and debris secure and away from the perimeter of the building.

- Outside lighting to aid security

- Closed-circuit television (CCTV), also known as video surveillance.

- Liaise with the Police for further advice on security and arson protection.

# Fire Alarm System

The Fire Alarm system, which incorporates; detectors, call points, wiring, sounders and main panel(s) must be tested in line with British Standard BS 5839.

If the alarm system is linked to a receiving centre then they should be contacted immediately before and after all tests.

The name and telephone number of the fire alarm service company responsible for maintenance should be displayed at the main control panel.

Failure to provide and maintain an appropriate fire alarm system could lead to formal enforcement under and may invalidate, or reduce, any claim made through an insurance company.

Detectors

The period between successive inspection and servicing visits should not exceed six months. Regular visual inspections of detectors should take place to check for damage, accumulations of dirt, heavy coats of paint and other conditions likely to interfere with the correct operation of the detector.

Daily Check

Inspect the panel for normal operation of the system. Where provided check that the connection of the remote manned centre is functioning correctly. Report any defect to a responsible person.

Weekly Test

Operate a trigger device (Manual Call Point or Detector) to sound the alarm, choosing alternatives on a strict rotational basis for subsequent weekly tests. Make a note of the device used and record in the log book. If accessible inspect batteries, generator and printer and carry out any necessary maintenance.

Monthly Test

If a generator is used start it up by simulation of a failure of the normal supply and allow it to run for at least one hour ensuring that fuel, oil and coolant levels are left topped up after the test.

Annual Inspection and Test

The false alarm/unwanted fire signals section should be checked by the installer/servicer and any faults to the system rectified.

The system should be inspected and tested by a competent person (usually an employee of the manufacturer or installer) in accordance with the current British Standard.

## Record of Fire Alarm Test

| Date | Test Zone | Fire Alarm Call Point / Detector | Automatic Door Release Satisfactory Yes / No | Results Fault & Remedial Action | Signature |
| --- | --- | --- | --- | --- | --- |

# Unwanted Fire Signals

Changes to British Standard 5839 now require users of automatic fire alarm systems to demonstrate satisfactory management of false alarms.

Failure to demonstrate satisfactory management of false alarms may lead to;

- Invalidate insurance policies.

- Charges being made for an attendance by the Fire and Rescue Service.

- Reduced attendance or non-attendance by the Fire and Rescue Service.

- Formal action taken under articles 13 and/or 17 of the RR (FS) O.

To demonstrate satisfactory management of false alarms, users must log and categorize the type of false alarm. False alarms fall into one of the following five categories;

Unwanted alarms

Alarms caused by fumes from cooking, steam, tobacco smoke, dust insects etc

Equipment false alarms

Alarms caused by faults with the equipment.

Malicious false alarms

Alarms arising from the unauthorized or malicious use of the equipment.

False alarms of good intent

These occur when an individual suspects there is a fire and raises the alarm

False alarms that do not fall into any of the above categories should be recorded as Unknown.

Recording this information enables your system installer/service provider to investigate any system faults/problems that you may have with your equipment.

## Record of False Fire Alarm Calls

| Date | Location | Category 1-5 | Brief Description Of Cause, Steam, Broken Glass Etc | Action Taken To Rectify/ Prevent Re- occurrence | Signature |
| --- | --- | --- | --- | --- | --- |

# Emergency Lighting System

The Emergency Lighting system, which incorporates; luminaires, wiring, batteries and or generators, must be tested. BS EN 50172:2024 requires the following testing;

Daily Check

Check that any previous faults have been rectified, that every lamp in a maintained unit is lit and that any control panel indicates normal. Ensure that any fault is recorded and acted upon.

Monthly Test

This can be done by simulation of a failure to the normal lighting supply. Allow sufficient time for all luminaries and signs to be checked and the result of such tests to be recorded in the logbook.

If a generator is used start it up by simulation of a failure of the normal supply and allow it to run for at least one hour ensuring that fuel, oil, and coolant levels are left topped up after the test.

The results to be recorded in the logbook.

Six Monthly/Annual Test

The system should be inspected and tested by a competent person (usually an employee of the manufacturer or installer) in accordance with the current British Standard. The results to be recorded in the logbook.

General

Existing illuminated signs with the words FIRE EXIT or EXIT no longer meet the EC Regulations. However, whilst the equipment functions correctly you may supplement it with the necessary signs incorporating a graphic symbol adjacent to it, this will ensure compliance.

For further information see British Standard BS 5266 Part 1 and Health & Safety (Signs and Signals) Regulations 1996 or consult your local fire safety officer.

## Record of Emergency Lighting System Test

| Date | Duration of test | Result of test | Fault (specify) | Fault cleared | Signature |
| --- | --- | --- | --- | --- | --- |

# Fire Fighting Equipment

Portable fire extinguishers, fire blankets and/or hose reels provided within your premises should be manufactured, sited and maintained in accordance with the accepted British or European equivalent standards, such as BS 5306-3:2017 and BS EN3.

Monthly Check

This is a simple visual check to ensure that all the extinguishers are in their proper positions and have not been discharged, lost pressure (those fitted with pressure indicators) or suffered any obvious damage. Make a note of the quantity, type and location of extinguishers that your premises contain and record in the logbook. A good practice is to also identify each extinguisher with a number, this will assist you in the ongoing management and maintenance of them.

As a rule fire extinguishers should be sited on exit routes, preferably near exit doors or where they are provided for specific risks, near to the hazards they protect. It is now also a requirement that the location of all firefighting equipment is identified by notices which contain a graphic symbol. See Health & Safety (Signs and Signals) Regulations 1996.

Annual Inspection

The annual inspection should be carried out by the contract service engineer or a suitably trained member of staff using the appropriate tools and manufacturers recommended procedures.

Intervals of discharge

The recommended times, in each case since the date of manufacture or the last actual discharge (test or otherwise) of the particular extinguisher body are as follows:

  - Water, Powder, Foam and Water based Foam, Every five years extended service and recharge if necessary.

  - Powder-Primary sealed. Every ten years extended service and recharge if necessary.

  - CO2. Overhauled and recharged every ten years.

Fire Blankets

Inspect and check to manufacturer’s instructions.

Hose Reels

Regular checks should be carried out by a responsible person to ensure that reels are unobstructed and show no obvious signs of leaks or corrosion. Thorough annual inspection and maintenance must be carried out as per BS EN 671-3:2009 pt 6.

These may be removed (cost and health risks are usually the reasons for removal) provided they are risk assessed out and suitable arrangements are in place to cover the risk.

## Record of Fire Fighting Equipment Test

| Date | Result of Inspection/Test Satisfactory/Faulty | Remedial Action Taken | Fault Rectified (Date) | Signature |
| --- | --- | --- | --- | --- |

# Fire Doors – Register and Maintenance

Fire doors are an important safety feature of any building in which people work or visit, as they offer resistance to the spread of fire and smoke limiting its effect. They are particularly important elements of fire protection on escape routes and as such must be monitored and maintain to ensure their effective operation.

Fire doors in your building what you need to know:

Prohibited - to wedge open, obstruct or interfere with a designated door.

Prohibited - to obstruct an automatically closing fire doors.

Prohibited - automatic door openers for mobility impaired persons on critical fire doors.

Prohibited- to cut or change a fire door drastically i.e. a split stable door.

Prohibited- Automatic door openers for mobility impaired persons on critical fire doors- not to be fitted on fire doors protecting escape routes or stair enclosures. (Seek further advice for clarification).

Vision Panels - should not be covered up or obstructed particularly in doors on circulation routes, from inner rooms, laboratories, or equipment rooms.

Approved Opening Devices – may be used in certain areas to hold fire doors open.

Mandatory - blue signs on fire doors to show that it is a fire door and a legal instruction to keep fire doors close.

Mandatory - doors that form workplace safety devices and systems must be subject to suitable System of inspections and maintenance.

Maintenance To assist in in the maintenance of fire doors and carrying out regular inspections the recording of the doors with a unique reference number along with location. (Some doors which are third party accredited will have a unique number on the top of the door). The maintenance inspection periods should be appropriate for the building and an assessment of the door usage, location, and footfall or heavy use by equipment for example trolleys.

  - Weekly check – very busy traffic routes with hundreds of openings a day;

  - Monthly check- traffic routes and main entrances and corridor doors;

  - Quarterly check- doors which do not have heavy use or sleeping accommodation;

  - Annually check- office or plant rooms low traffic and use.

Inspection Fire Doors

Points to check on fire doors.

  - Seek confirmation that the door has been certified or has been accredited to be a fire door.

- Ensure there is no damage, defects or warping to the frame or securing wall.

  - Make sure the door body (leaf) has not been damaged, warped or twisted.

  - Ensure it closes correctly around all parts of the frame.

  - Check that the closer shuts the door onto the latch, from any open position.

  - Check the gap around the door to the frame is constantly between 2 to 4mm.

  - Check the three hinges are firmly fixed into the door and frame with no missing screws.

  - Ensure that the intumescent strips seals and cold smoke seals at the top and sides of the door or frame are not damaged or missing.

  - Make sure any glass and the beads holding the glass are fitted firmly with no visible damage.

  - Make sure the door is not wedged open as this will cause damage to the hinges over time and the door will fail to close properly in its frame. Look for evidence of this practice occurring.

  - Check that the door is marked correctly with appropriate signage.

  - If the door has a letter box, ensure it is suitably closed and it suitable for use in fire-resisting doors.

## Record of Door Check Test

Note best practice will be to identify each door with a reference number which reflects their location within the building.

| Date | Location |  |  | Checks Completed |  |  |  |  |  |  |  |  |  |  | Comments – Details of issues identified |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Floor | Door | Door Type | Certified / Accredited | Door, Frame & Securing Wall | Letter- box | Glazing | Hinges & Locks | Door Gaps (2-4mm) | Strips & Seals | Self-Closing | Door Wedged Open | Signage | Any Other Damage |  |

### Action Plan

| Door Identifier (Floor/Door/Door Type) | Issues/Deficiency Identified | Proposed Action | Timescales (Date) | Person Responsible |
| --- | --- | --- | --- | --- |

# Acoustic Fire Door Holders Testing

To comply with B.S.EN 1155:1997.Harmonised European standard which specifies requirements for separate hold open mechanisms incorporated in a door closer intended to be used on fire /smoke doors.

- AFDH is not releasing upon the Fire Alarm actuation

    - Check fire alarm sounds for at least 30 seconds.

    - Check door is free to close unhindered. (See manufacturer’s instructions).

- AFDH releases to no apparent sound

As a safety feature, AFDH has to release to any sound that it hears as being continuous and loud as this sound could be obscuring a potential fire alarm. (See manufacturer’s instructions).

- AFDH does not retain the door in an open position

Check that the plunger is depressed.

Check that the battery compartment is closed and that the batteries are effective. Check that AFDH is not fitted too low on the door. (See manufacturer’s instructions)

- Replace batteries when required and record. (See manufacturer’s instructions)

  - If not required to be left open for usage then they should be left shut.

It is recommended that fire doors are kept closed at night, as the chance of a fire spreading undetected is greater than during daylight hours.

If a wireless connection is used between devices, then they need to comply with BS 7273-4

## Record of Acoustic Fire Door Holders Test

(“Door guard etc.”)

Dependent on your Fire Risk Assessment these are suited for retrofit installations but should generally not be used on fire doors leading onto staircases or other critical areas. Best practice is to number each Acoustic Fire Door Holder (AFDH) with Location.

Tested weekly with the fire alarm test.

| Date | AFDH Number/location | Faults | Fault Rectified (Date) | Signature |
| --- | --- | --- | --- | --- |

# Sprinkler Systems

General

Automatic sprinklers may be conditional to the insurance policy of premises and as such should be maintained in accordance with the terms and conditions of the insurance policy to ensure full and adequate protection.

In addition, a sprinkler system may form part of an engineered solution or compensation for departure from normally accepted fire safety standards or building regulations. As such, the sprinkler system must be maintained to ensure those departures are consistent with the Fire Safety Risk assessment. Where a sprinkler system forms part of an engineered solution it may also be subject to an Alterations Notice, under article 29 of the RR (FS) O, and the maintenance requirements of article 17 of the RR (FS) O

The installer of the Automatic Fire Sprinkler System should provide to the occupier an inspection and programme of checks for the system. The programme should include; instruction on the action to be taken in respect of faults, operation of the system, in particular the procedure for emergency manual starting of any pumps and details of daily and weekly routines.

Weekly

The following checks shall be made and recorded;

- All water and air pressure gauge readings on installations, trunk mains and pressure tanks

- All water levels in elevated private reservoirs, rivers, lakes and water storage tanks.

Water Motor Alarm Test

Each water motor alarm shall be sounded for not less than 30 seconds

Automatic Pump Starting Test

Test on automatic pumps shall include;

- Check fuel and engine lubricating levels

- Reduce water pressure on starting device to simulate condition of auto-start

- Record the starting (cut-in) pressure and check it is correct.

Quarterly / Six Monthly / Annual Routines

The service and maintenance schedules detailed in the current British Standard should be carried by a competent person who will supply the user with a signed and dated report of the inspection.

## Record of Sprinkler System Test

| Normal Gauge Pressure Range | Water Gauge |  | Air Pressure |  | Pump Cut-In Pressure | Diesel Engine Restart | Batteries | Stop Valves Zone Valves | Signature |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Satisfactory Yes/No |  | Satisfactory Yes/No |  |  |  |  |  |  |
| Date |  |  |  |  |  |  |  |  |  |

# Smoke Ventilation Systems

Smoke ventilations systems may be provided as part of an engineered solution and as such may be subject to an Alterations Notice, under article 29 of the RR (FS) O and the maintenance requirements of Article 17 of the RR (FS) O. Furthermore, if the smoke ventilation system is provided for the assistance of fire-fighting purposes, it will also be subject to Article 38 of the RR (FS) O.

The ventilation system test should be carried out in accordance with the manufacturer’s instructions, in order to meet the requirements of the current British or European equivalent, standards.

Weekly

During the Fire Alarm test, check that all smoke ventilators and smoke curtains have operated correctly and they are properly re-set at the conclusion of the test.

Annually

The system should be tested by a specialist engineer in accordance with the current British or European equivalent, standards.

## Record of Smoke Ventilation System Test

| Date of Tests | Curtains / Ventilators |  | Compressor |  | Annual Service / Test | Signature |
| --- | --- | --- | --- | --- | --- | --- |
|  | Satisfactory | Unsatisfactory | Receiver Pressure | Hours Run Meter |  |  |

# Fire Fighting Provisions

General

In accordance with Article 17 and Article 38 of the Regulatory Reform (Fire Safety) Order 2005, and Regulation 7 of the Fire Safety (England) Regulations 2022, certain facilities provided to assist the Fire and Rescue Service, or to support evacuation and firefighting operations, are classed as essential firefighting equipment and are required to be subject to a suitable system of inspection, testing and maintenance.

Where provided, the following systems must be inspected and tested at the frequency specified, and the	results recorded within this logbook.

- Firefighting Lifts and Evacuation Lifts

Firefighting lifts and evacuation lifts may be provided as part of the building’s fire safety strategy to assist the Fire and Rescue Service and/or to facilitate the evacuation of relevant persons.

Where provided, these lifts are subject to the maintenance requirements of Article 17 and Article 38 of the RR (FS) O and the monthly testing requirements of Regulation 7.

Monthly Test

A monthly test shall be carried out to confirm that:

- The lift is operational and available for use

- Firefighter controls operate correctly

- The lift responds correctly when recalled by the fire alarm system

- Communication systems within the lift car are operational

- Any signage and instructions are present and legible

Any defects identified must be recorded and remedial action taken without undue delay.

- Dry and Wet Rising Mains

Dry and wet rising mains are provided to assist the Fire and Rescue Service in delivering water to upper floors of a building. These systems are subject to Article 38 of the RR (FS) O and Regulation 7 of the Fire Safety (England) Regulations.

Monthly Test

The monthly check should include:

- Visual inspection of all inlet and outlet boxes

- Confirmation that caps, valves and securing chains are present and undamaged

- Verification that outlets are unobstructed and clearly labelled

- Checking for signs of damage, corrosion or leakage

Any faults identified must be recorded and reported for repair.

- Smoke Control / Smoke Ventilation Systems

Smoke ventilation systems may be provided as part of an engineered fire safety solution and may be subject to an Alterations Notice under Article 29, the maintenance requirements of Article 17, and where provided for firefighting purposes, Article 38 of the RR (FS) O.

In addition to weekly functional checks, smoke control systems are classed as essential firefighting equipment and are subject to monthly inspection and testing in accordance with Regulation 7.

Monthly Test

The monthly test should confirm that:

- Smoke ventilators, dampers, fans and controls operate correctly

- Interfaces with the fire detection and alarm system function as intended

- Any manual override controls are accessible and operational

- The system resets correctly following activation

Results of the test must be recorded in the logbook.

- Suppression Systems (Including Sprinklers or Other Fixed Systems)

In addition to weekly and periodic testing, fixed fire suppression systems provided for firefighting or life safety purposes are classed as essential firefighting equipment and are subject to monthly inspection under Regulation 7.

Monthly Check

The monthly check should include:

- Visual inspection of control valves and indicators

- Confirmation that systems are in service and unobstructed

- Checking pumps, power supplies and alarms for normal condition

- Verification that no alterations or impairments are present

Any defects must be recorded and reported to the service provider.

- Fire Detection and Fire Alarm Systems (Monthly Requirement)

In addition to weekly user testing, the fire detection and fire alarm system, including any detectors or interfaces linked to ancillary systems such as smoke control systems, must be subject to a monthly inspection in accordance with Regulation 7.

Monthly Inspection

The monthly inspection should include:

- Review of fault logs and system history

- Confirmation that interfaces with ancillary systems operate correctly

- Verification that automatic door releases, smoke control interfaces and lift controls respond correctly

- Confirmation that any outstanding defects are being managed

The inspection and any actions taken must be recorded in the logbook.

- Evacuation Alert Systems

Evacuation alert systems may be provided in buildings to allow the Fire and Rescue Service to initiate evacuation of specific areas. Where provided, these systems are subject to Articles 17 and 38 of the RR (FS) O and Regulation 7.

Monthly Test

The monthly test should confirm that:

- Control and indication equipment is operational

- Alert signals operate correctly in designated areas

- Power supplies and fault indicators show normal condition

- Controls are secure and accessible only to authorised persons

Results must be recorded and defects rectified without delay.

## Record of Fire Fighting Provisions Test

| Date | Location | Equipment Type | Checks Completed |  |  |  |  |  |  | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Firefighting Lifts and Evacuation Lifts | The lift is operational and available for use |  |  |  |  |  |  |  |
|  |  |  | Firefighter controls operate correctly |  |  |  |  |  |  |  |
|  |  |  | The lift responds correctly when recalled by the fire alarm system |  |  |  |  |  |  |  |
|  |  |  | Communication systems within the lift car are operational |  |  |  |  |  |  |  |
|  |  |  | Any signage and instructions are present and legible |  |  |  |  |  |  |  |
|  |  | Dry and Wet Rising Mains | Visual inspection of all inlet and outlet boxes |  |  |  |  |  |  |  |
|  |  |  | Confirmation that caps, valves and securing chains are present and undamaged |  |  |  |  |  |  |  |
|  |  |  | Verification that outlets are unobstructed and clearly labelled |  |  |  |  |  |  |  |
|  |  |  | Checking for signs of damage, corrosion or leakage |  |  |  |  |  |  |  |
|  |  | Smoke Control / Smoke Ventilation Systems | Smoke ventilators, dampers, fans and controls operate correctly |  |  |  |  |  |  |  |
|  |  |  | Interfaces with the fire detection and alarm system function as intended |  |  |  |  |  |  |  |
|  |  |  | Any manual override controls are accessible and operational |  |  |  |  |  |  |  |
|  |  |  | The system resets correctly following activation |  |  |  |  |  |  |  |

| Date | Location | Equipment Type | Checks Completed |  |  |  |  |  |  | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Suppression Systems (Including Sprinklers or Other Fixed Systems) | Visual inspection of control valves and indicators |  |  |  |  |  |  |  |
|  |  |  | Confirmation that systems are in service and unobstructed |  |  |  |  |  |  |  |
|  |  |  | Checking pumps, power supplies and alarms for normal condition |  |  |  |  |  |  |  |
|  |  |  | Verification that no alterations or impairments are present |  |  |  |  |  |  |  |
|  |  | Fire Detection and Fire Alarm Systems (Monthly Requirement) | Review of fault logs and system history |  |  |  |  |  |  |  |
|  |  |  | Confirmation that interfaces with ancillary systems operate correctly |  |  |  |  |  |  |  |
|  |  |  | Verification that automatic door releases, smoke control interfaces and lift controls respond correctly |  |  |  |  |  |  |  |
|  |  |  | Confirmation that any outstanding defects are being managed |  |  |  |  |  |  |  |
|  |  | Evacuation Alert Systems | Control and indication equipment is operational |  |  |  |  |  |  |  |
|  |  |  | Alert signals operate correctly in designated areas |  |  |  |  |  |  |  |
|  |  |  | Power supplies and fault indicators show normal condition |  |  |  |  |  |  |  |
|  |  |  | Controls are secure and accessible only to authorised persons |  |  |  |  |  |  |  |

| Equipment Type | Issues/Deficiency Identified | Proposed Action | Timescales (Date) | Person Responsible |
| --- | --- | --- | --- | --- |

### Action Plan

# Fire Instruction and Training

It is important that all staff should receive basic fire training in what to do in the event of fire, including those who work irregular hours, part time or casually employed.

Article 21.1 Regulatory Reform (Fire Safety) Order 2005

The responsible person must ensure that his employees are provided with adequate safety training.

The training should focus on the following general areas:

Actions to be taken in the event of fire - how to raise the alarm.

Evacuation Procedures - identifying the location and use of escape routes, fire alarm call points, firefighting equipment and nominated assembly points.

How to call the Fire Service - premises procedures.

In addition to the above, certain members of staff in large buildings may also be nominated to carry out specific tasks in the event of fire and these should also be incorporated to ensure procedures are carried out efficiently and safely.

All staff should receive information and training on the fire safety provisions within the premises as soon as possible after being appointed and at regular intervals thereafter, (at least annually). The information given should be based on your emergency action plan and must include:

  - The significant findings of your fire risk assessment

  - Staff fire procedures.

  - The identity of persons with responsibilities for fire safety: - fire wardens etc.

  - The measures that are in place to reduce/mitigate the effects of fire.

  - Any special arrangements that are in place

  - The location of emergency exits and fire-fighting equipment (and the use of if appropriate).

## Record of Staff Training / Instruction

| Date | Instruction Duration | Person Receiving Instruction | Signature of Person | Nature of Instruction | Signature of Instructor |
| --- | --- | --- | --- | --- | --- |

# Fire Evacuations and Drills

Drills should be conducted to simulate fire conditions and to test fire procedures and all staff should be conversant with the premises evacuation procedures and take part in fire evacuation drills at least once and preferably twice per year.

Article 15.1 Regulatory Reform (Fire Safety) Order 2005

The responsible person must establish and, where necessary, give effect to appropriate procedures, including safety drills, to be followed in the event of serious and imminent danger to relevant persons.

Fire Drills and practice evacuations should not be used to embarrass staff or unduly inconvenience people. However, they are crucial in testing local procedures for evacuating the premises and highlighting problem areas which may need addressing.

Ideally, most people should be aware that a fire drill is due to take place, to minimise any adverse effects and provide staff with time to ensure they are familiar with alternative exit routes. It may not always be possible to alert everyone, especially if the premises have relatively open access or are used by the public.

Debriefs on the effectiveness of the drills should be carried out so that any evacuation procedures can be changed if necessary.

| Date and Time | Person Responsible for Drill | Number of Staff Involved | Time Taken to Evacuate | Optimum time to Evacuate |
| --- | --- | --- | --- | --- |
| Simulation (i.e. normal toute blocked / fire in foyer) |  |  |  |  |
| Assessment of Drill |  |  |  |  |
| Recommendations or further actions required |  |  |  |  |

## Record of Fire Drills / Evacuations

| Date | Nature of Drill | Persons/Sections Taking Part | Evacuation Time | Person in Charge | Signature |
| --- | --- | --- | --- | --- | --- |

# Fire Safety Risk Assessment

It is necessary for the responsible person to ensure that a suitable and sufficient risk assessment of the risk of fire is carried out.

Article 9.1 Regulatory Reform (Fire Safety) Order 2005

The responsible person must make a suitable and sufficient assessment of the risks to which relevant persons are exposed for the purposes of identifying the general fire precautions he needs to take

All premises should have a fire risk assessment if they are a place of work.

It is necessary for the risk assessment to be updated and review annually more frequently if the below circumstances apply:

Article 9.3 Regulatory Reform (Fire Safety) Order 2005

Any such assessment must be reviewed by the responsible person regularly so as to keep it up to date and particularly if:

- There is reason to suspect that it is no longer valid

- There has been a significant change in relation to the premises, special, technical and organisational measures; or significant structural changes such as extension or conversions.

The following table can be used as a record of when a Fire Safety Risk assessment is carried out and when the next risk assessment is due.

## Record of Fire Safety Risk Assessment

| Date Risk Assessment Carried Out | Name of Person Conducting Risk Assessment | Brief Comments | Date Next Due |
| --- | --- | --- | --- |

Further information and guidance is available in Part 1 of the series of fire safety guides published by the Department for Communities and Local Government and available to download from www.communities.gov.uk/ or to purchase from your nearest TSO outlet.

# Business Continuity and Planning

Fires in industrial and commercial premises can have a serious impact on both national and local economy. There is a risk of significant job losses with subsequent social and economic impact on the community as well as environmental damage.

When considering incidents at premises for the purpose of business continuity it should be borne in mind that approximately 60% of all companies involved in a serious fire are unable to re-start after the fire. Many businesses that experience a serious fire do not recover. Significant parts of the building or premises may have been affected and could remain unusable for some time.

By taking a short moment to consider the impact that a fire might have on your business, you may be able to minimize the impact and ensure survival of your business in the longer term, as well as the survival of people and property in the short term.

The following is intended as prompt rather than a full record of contacts and record of documentations.

List of Considerations and Actions for Business Continuity Following Disruption

| Consideration | Satisfactory Yes / No | Further Action Required |
| --- | --- | --- |
| Salvage plan prepared and held in secure location away from main premises |  |  |
| Contract agreements in place and up to date for fire / flood restoration |  |  |
| Computer files backed up daily to separate server / location away from main building |  |  |
| Temporary accommodation ear-marked and available |  |  |
| Alternate service provider(s) listed to maintain customer continuity |  |  |
| Insurance policy checked for cover against loss of revenue and relocation |  |  |
| List of emergency contacts up to date and available |  |  |
| Other Considerations |  |  |
| Other Considerations |  |  |
| Other Considerations |  |  |